## Sheet1
LOADINGS OF POWER TRANSFORMERS FOR THE MONTH OF MAY 2018
Sr. No. | Name and configuration of Substation | No of Power Transformers and Capacity | Loading in MVA of each Power Transformer
|  |  | Peak | Off Peak
1 | 2 | 3 | 4 | 5
Division-VII, Curchorem
| 33/11KV, 2 x 10MVA Pontemol Sub-station | 10MVA-1 No | 5.15 | 3.15
|  | 10MVA-1 No | 4.57 | 2.4
| 33/11KV, 1x3.15MVA, Quinamol sub-station | 3.15MVA-1 No | 0.97 | 0.62
| 33/11 KV ,1x6.3 MVA Xelpem Sub-station | 6.3 MVA - 1 No | 3.77 | 2.46
| 33/11 KV ,1x3.15 MVA Waddem Sub-station | 3.15 MVA - 1 No | 2.86 | 0.29
| 33/11KV, 1x 6.3MVA, Shigao Substation | 6.3MVA- 1 No | 1.5 | 1.05
Division- XIII, Kadamba Plateau
| 110/33 KV Kadamba S/S (EHV) | Transf #1 | 36 MVA | 9.5 MVA
|  | Transf #2 | 38 MVA | 0 MVA
|  | Transf #3 | 40 MVA | 6.2 MVA
|  | Transf #4 | 35 MVA | 7.6 MVA
NOTE: All the Power transformers were not loaded to maximum on the same day and the maximum loading of the substation was about 85 MVA during May, 2018.
Division-XI, Vasco
| 33/11KV Harbour Sub-Station | 6.3 MVA - 02 Nos
|  | TR-I | 76 | 64 | 33KV Side
|  | TR-II | 84 | 73
| 33/11KV Kadamba Sub-Station | 6.3 MVA - 02 Nos
|  | TR-I | 98 | 76 | 33KV Side
|  | TR-II | 99 | 74
| 33/11KV Sancoale Sub-Station | 6.3 MVA - 04 Nos
|  | TR-1 | 65 | 32 | 33KV Side
|  | TR-2 | 80 | 32
|  | TR-3 | 45 | 24
|  | TR-4 | 53 | 29
| 110/33/11KV Verna Sub-Station | 10 MVA | 120 | 52 | 33KV Side
|  | 6.3MVA I | 100 | 60
|  | 6.3MVA II | 100 | 60
| 33/11KV Majorda Sub-Station | 10 MVA | 72 | 30 | 33 KV Side
|  | 6.3MVA | 70 | 42
| 110/33/11KV Verna Sub-Station | 50 MVA | 210 | 140 | 110 KV Side
|  | 40 MVA I | 198 | 135
|  | 40 MVA II | 147 | 117
Note: Peak Load restricted ( PLR) implemented due to overloading of lines & Power Transformers ( Verna Sub-Station- Div.XIV)
Division-III, Ponda
| 220KV/110KV/33KV Ponda Sub-station | 10Nos | - | -
|  | 1) 220/110KV, 100 MVA-I | (454 Amp) 77 MW | (223 Amp) 42 MW
|  | 2) 220/110KV, 100 MVA-II | (370 Amp) 64 MW | (180 Amp) 32 MW
|  | 3) 220/110KV, 100 MVA-III | (310 Amp) 52 MW | (72 Amp) 12 MW
|  | 4) 220/33KV, 50 MVA | (660 Amp) 37 MW | (230 Amp) 13MW
|  | 5) 110/33KV, 40 MVA-I | (50 Amp) 31 MW | (225 Amp) 13 MW
|  | 6) 110/33KV, 40 MVA-II | (684 Amp) 38 MW | (225 Amp) 13 MW
|  | 7) 110/33KV, 30 MVA-I | (360 Amp) 20 MW | (180 Amp) 10 MW
|  | *8) 110/33KV, 30 MVA-II | (216 Amp) 12 MW | (180 Amp) 10 MW
|  | 9) 110/33KV, 30 MVA-III | (395 Amp) 22 MW | (200 Amp) 12 MW
|  | 10) 33/11KV, 6.3 MVA | (70 Amp) 4 MW | (45 Amp) 2.5 MW
*Due to insulation problem, 110/33KV, 30MVA -II is being used for 33/11KV tranformation for local 11KV feed.
Division-XI, Tivim
| 220/33/11 KV , 50MVAX2 , 1x6.3 MVA Amona Sub-station in Bicholim taluka | 1) 50 MVA- I | 28.7 | 21.2
|  | 2) 50 MVA- II | 22.96 | 15.6
|  | 3) 6.3 MVA | 1.9 | 1.1
| 220/110/33/11 KV , (3 x 100 MVA 220/110 KV, 2 x 50 MVA and 2 x 40 MVA, 110/33 KV, 2 x 10 MVA, 33/11 KV) | 3 x 100 MVA, 220/110 KV (Connected in parallel) | 217 | 161
|  | 40 MVA, 110/33 KV Tr - 1 | 27.93 | 18.52
|  | 50 MVA, 110/33 KV Tr - 2 | 34.21 | 25.21
|  | 40 MVA, 110/33 KV Tr - 3 | 31.64 | 24.69
|  | 50 MVA, 110/33 KV Tr - 4 | 39.61 | 30.35
|  | 10 MVA, 33/11 KV Tr - 1 | 3.4 | 3.29
|  | 10 MVA, 33/11 KV Tr - 2 | 5.04 | 1.75
Division-XVI, Margao
Sub Div.-I, Benaulim
| 33/11KV Benaulim S/S | i) 6.3MVA | 91.3Amps | 47.3Amps
|  | ii) 6.3MVA | 80Amps | 41.6Amps
|  | iii) 6.3MVA | 78.3Amps | 54Amps
| 33/11KV Carmona | i) 6.3MVA | 75.3Amps | 37.6Amps
Sub Div. II, Chinchinim
| 33/11KV Velim S/S | i) 6.3MVA | 10Amps | 5Amps
|  | ii) 6.3MVA | 58Amps | 28Amps
Sub Div.-III, Canacona
| 33/11KV Canacona S/S | i) 6.3MVA | 66.6Amps | 43.3Amps
|  | ii) 6.3MVA | 55Amps | 40Amps
| 33/11KV Muthal/Paiguinim | i) 6.3MVA | 46.6Amps | 30Amps
Sub Div.-IV, Cuncolim
| 33/11KV Cuncolim S/S | i) 6.3MVA | 85Amps | 75Amps
|  | ii) 6.3MVA | 86Amps | 78Amps
|  | iii) 10MVA | 95Amps | 80Amps
Division-XII, Xeldem
| 33/11 KV 6.3 MVA Xeldem Substation | 6.3 MVA – 1 No. | 5.25 (11 KV Peak hour loading -276 A) | 2.85 (11 KV Off peak hour loading – 150a)
| 220/110/33/11 KV Xeldem Substation | 100 MVA –I | 65.72 (110 KV Peak hour loading -345 A) | 40.00 (110 KV Off peak hour loading – 210 A)
| 220/110/33/11 KV Xeldem Substation | 100 MVA –II | 72.39 (110 KV Peak hour loading -380 A) | 45.72 (110 KV Off peak hour loading – 240 A)
| 220/110/33/11 KV Xeldem Substation | 50 MVA | 31.43 (33 KV Peak hour loading -530 A) | 16.00 (33 KV Off peak hour loading – 280 A)
| 220/110/33/11 KV Xeldem Substation | 40 MVA – I | 32.23 (33 KV Peak hour loading -564 A) | 18.28 (33 KV Off peak hour loading – 320 A)
| 220/110/33/11 KV Xeldem Substation | 40 MVA – II | 32.23 (33 KV Peak hour loading -564 A) | 18.28 (33 KV Off peak hour loading – 320 A)
Division-X, Ponda
| 33/11KV Colony S/S Sub div - I Div-X Ponda | Sl No 8973-1 Capacity:-6.3 MVA Make:- Voltamp Transformer ltd Baroda Year of Mfg:- 2007 | 4.44 (20.00 Hrs) | 2.42 (07.00 Hrs)
|  | Sl No. 21264/2 Capacity:-6.3 MVA Make:- Voltamp Transformer ltd Baroda Year of Mfg:- 2009 | 3.91 (23.00 Hrs) | 2.19 (07.00 Hrs)
| 33/11KV Dharbandora S/S Sub div - II Div-X Ponda | Sl No. MT 4556 Capacity:-6.3 MVA Make:- CGL ltd Year of Mfg:- 2002 | 4.66 (20.00 Hrs) | 3.14 (12.00 Hrs)
| 33/11KV Bethora S/S Sub div - II Div-X Ponda | Sl No. B-2831 Capacity:-6.3 MVA Make:- Alstom Year of Mfg:- 2000 | 4.18 (12.00 Hrs) | 3.71 (20.00 Hrs)
| 33/11KV Shiroda S/S Sub div - II Div-X Ponda | Sl No. KT-6300/23 Capacity:-6.3 MVA Make:- Kanohar Year of Mfg:- 2007 | 3.42 (20.00 Hrs) | 2.09 (12.00 Hrs)
| 33/11KV Kundai S/S Sub div - III Div-X Ponda | Sl No 600005720 Capacity :-10MVA (I) Make:- Viajay Electricals Year of Mfg;- 2011 | 8.9 ( 11.00 Hrs ) | 3.76 ( 16.00 Hrs )
|  | Sl No 600005721 Capacity :-10MVA (2) Make:- Viajay Electricals Year of Mfg:- 2011 | 5.31 (12.00 )Hrs | 3.19 ( 15.00 Hrs)
| 33/11KV Madkai S/S Sub div - III Div-X Ponda | Sl No:-1796 Capacity :-6.3MVA Make:- Emco Ltd Year of Mfg:- 2006 | 5.8 (20.00 Hrs ) | 5.65 (01.00 Hrs)
Division-V, Bicholim
| 33/11 KV , 3x6.3 MVA Bicholim Sub-station | 6.3 MVA(I) - 1 No | 5.23 (Peak hour loading - 275 A) | 2.03 (Off Peak hour loading - 107 A)
|  | 6.3 MVA(II) - 1 No | 4.84 (Peak hour loading - 257 A) | 1.92 (Off Peak hour loading - 101 A)
|  | 6.3 MVA(III) - 1 No | 4.42 (Peak hour loading - 232 A) | 1.96 (Off Peak hour loading - 103 A)
| 33/11 KV , 1x10 MVA, Sankhali Sub-station | 10 MVA - 1 No. | 6.91 (Peak hour loading - 363 A) | 3.1 (Off Peak hour loading - 163 A)
| 33/11 KV , 1x6.3 MVA Pale Sub-station | 6.3 MVA - 1 No | 1.71 (Peak hour loading - 90 A) | 0.86 (Off Peak hour loading - 45 A)
| 33/11 KV , 2x6.3 MVA Valpoi Sub-station | 6.3 MVA(I) - 1 No | 4.13 (Peak hour loading - 217 A) | 2.78 (Off Peak hour loading - 146 A)
|  | 6.3 MVA(II) - 1 No | 2.95 (Peak hour loading - 155 A) | 2.61 (Off Peak hour loading - 137 A)
Division-I, Panaji
| Corlim Substation | 6.3 MVA-I | 95 | 65
|  | 6.3 MVA-I | 95 | 70
|  | 3.15 | 45 | 30
| Altinho Substation | (Transf -1) 6.3 | 78 | 24
|  | (Transf -2) 6.3 | 83 | 27
|  | (Transf -3) 8 | 111 | 43
| EDC | (Transf -1) 6.3 | 106 | 28
|  | (Transf -2) 8 | 101 | 28
| Campal | (Transf -1) 10 | 142 | 44
|  | (Transf -2) 6.3 | 64 | 18
| Bambolim | 6.3 MVA-I | 95 | 60
|  | 6.3 MVA-II | 96 | 65
| Pilar | 6.3 MVA-I | 90 | 50
|  | 3.15 | Is under repair
| Nagali Hill | 10 MVA | 144 | 80
| NIO Substation | 6.3 MVA | 82 | 50
Division-XVII, Mapusa
| Pernem-Sub station | Incomer - I 6.3 MVA Transformer - I | 5.3 MVA | 5.1 MVA
| Pernem-Sub station | Incomer - II 6.3 MVA Transformer - II | 5.1 MVA | 4.9 MVA
| 6.3MVA 33/11KV Nachinola S/S | 6.3/8 MVA-1 No | 6.5 MVA (Peak hour loading - 352 A 11 KV Side) | 4.8 MVA (Off Peak hour loading - 252 A 11 KV side)
| ---- | ----- | 117 A - 3 KV Side | 85 A - 33 side
| ---- | 6.3 MVA- 1 No failed in June -2017( Transformer was repaired earlier 7 is also very old-1987 Model, hence, Proposed for new only) | ---- | ----
| 2 X 6.3MVA 33/11KV Tuem S/S | 6.3 MVA-1 No | 3.37 MVA (Peak hour loading on 11KV - 192 A) Tuem feeder being fed from Pernem Sub Station due to overloading issue | 2.1 MVA (Off Peak hour loading 11KV - 120 A)
|  | 6.3 MVA-2 No | 2.84 MVA (Peak hour loading on 11KV - 164 A) Tuem I.D.C feeder being fed from Pernem Substation due to overloading issue. | 1.47 MVA (Off Peak hour loading 11KV - 85 A)
Division-IV, Margao
| 33/11KV Aquem Sub-station | TR-1, 10MVA (new) | 133 A | 113 A
|  | TR-II, 10MVA | 137 A | 121 A
| 33/11KV Monte Sub-station | TR-I | 88 A | 81 A
|  | TR-II | 88 A | 84 A
|  | TR-III, 6.3MVA | 68 A | 59 A
| 33/11KV Fatorda Sub-station | TR-I, 10MVA | 226 A | 133 A
|  | TR-II, 6.3MVA | 209 A | 122 A
|  | TR-III, 6.3MVA | 373 A | 208 A
| 33/11KV KRC Sub-station | TR1, 10MVA (new) | 124 A | 74 A
|  | TR-II, 6.3MVA | No Load | No Load
| 33/11KV Nessai Sub-station | TR-I, 6.3MVA | 71 A | 51 A
|  | TR-II, 6.3MVA | 67 A | 47 A
| 33/11KV Raia Sub-station | TR-I, 6.3MVA | 143 A | 70 A
|  | TR-II, 6.3MVA | 264 A | 144 A
Division-VI, Mapusa
S/D-I(U) Mapusa
1 | Mapusa Sub-Station | 10MVA -I | 9.5 | 7.9
2 |  | 10MVA -II | 7.9 | 6.8
3 |  | 10MVA- III | 9.4 | 7.8
4 |  | 8MVA | 7.2 | 6.4
S/D-II Porvorim
1 | Porvorim Sub-Station | 6.3MVA | 276 A | 251 A
2 |  | 8 MVA | 273 A | 241 A
3 |  | 10 MVA | 461 A | 425 A
S/D-III Mapusa
1 | Nagoa Sub-Station | 8 MVA | 7.31 | 6.15
2 |  | 6.3 MVA | 5.83 | 3.88
3 |  | 10 MVA | 8.91 | 6.63
S/D-IV Calangute
1 | Saligao Substation | 6.3MVA | 3.14 | 3.1
2 |  | 6.3/8MVA | 4.23 | 4.19
3 |  | 10MVA | 6.34 | 6.02
4 | Candolim substation | 6.3MVA | 5.12 | 5.02
5 |  | 6.3/8MVA | 6.31 | 6.23