## Sheet1
LOADINGS OF POWER TRANSFORMERS FOR THE MONTH OF MAY 2019
Sr. No. | Name and configuration of Substation | No of Power Transformers and Capacity | Loading in MVA / Amps of each Power Transformer
|  |  | Peak | Off Peak
1 | 2 | 3 | 4 | 5
Division-VII, Curchorem | [5 empty] | 2019-05-01
| 33/11KV, 2 x 10MVA Pontemol Sub-station | 10MVA-1 No | 5.5 | 3.3
|  | 10MVA-1 No | 4.9 | 2.6
| 33/11KV, 1x3.15MVA, Quinamol sub-station | 3.15MVA-1 No | 1.94 | 0.47
| 33/11 KV ,1x6.3 MVA Xelpem Sub-station | 6.3 MVA - 1 No | 3.43 | 2.29
| 33/11 KV ,1x3.15 MVA Waddem Sub-station | 3.15 MVA - 1 No | 2.97 | 1.03
| 33/11KV, 1x 6.3MVA, Shigao Substation | 6.3MVA- 1 No | 1.54 | 0.91
Division- XIII, Kadamba Plateau | [5 empty] | 2019-05-01
| 110/33 KV Kadamba S/S (EHV) | Transf #1 40MVA | 99 amps (18 MW) | 60 amps (3.24 MW) |  | 99 | 99 | 1.7321 | 11000 | 1 | 1886203.3294 | 1.8862
|  | Transf #2 40MVA | 203 amps (37 MW) | 109 amps (20 MW) |  | 203 | 0.203 | 1.7321 | 11000 | 1 | 3867.6695
|  | Transf #3 40MVA | 182 amps (33 MW) | 58 amps (10.5 MW) |  | 182 | 0.182 | 1.7321 | 11000 | 1 | 3467.5657
|  | Transf #4 40MVA | 177 amps (32 MW) | 37 amps (7 MW) |  | 177 | 0.177 | 1.7321 | 11000 | 1 | 3372.3029
Division-XI, Vasco | [5 empty] | 2019-05-01
| 33/11KV Harbour Sub-Station | 6.3 MVA - 02 Nos
|  | TR - I | 84 | 48 | 33KV Side
|  | TR - II | 89 | 56
| 33/11KV Kadamba Sub-Station | 6.3 MVA - 02 Nos
|  | TR - I | 98 | 87 | 33KV Side
|  | TR - II | 96 | 79
| 33/11KV Sancoale Sub-Station | 6.3 MVA - 04 Nos
|  | TR - I | 60 | 38 | 33KV Side
|  | TR - II | 70 | 52
|  | TR - III | 48 | 36
|  | TR - IV | 60 | 45
Division-III, Ponda | [5 empty] | 2019-05-01
| 220KV/110KV/33KV Ponda Sub-station | 10Nos | - | -
|  | 1) 220/110KV, 100 MVA-I | (435 Amp)72.5 MW | (448 Amp)74.7 MW
|  | 2) 220/110KV, 100 MVA-II | (370 Amp) 61.7 MW | (410 Amp)68.3 MW
|  | 3) 220/110KV, 100 MVA-III | (368 Amp) 61.3 MW | (422 Amp)70.3 MW
|  | 4) 220/33KV, 50 MVA | (640 Amp)35.6 MW | (630 Amp) 35 MW
|  | 5) 110/33KV, 40 MVA-I | (545 Amp)30.3 MW | (500 Amp) 27.8 MW
|  | 6) 110/33KV, 40 MVA-II | (505 Amp)28.1 MW | (513 Amp) 28.5 MW
|  | 7) 110/33KV, 30 MVA-I | (330 Amp) 18.3 MW | (362 Amp)20.1 MW
|  | *8) 110/33KV, 30 MVA-II | (85 Amp) 4.7 MW | (85 Amp) 4.7 MW
|  | 9) 110/33KV, 30 MVA-III | (420 Amp) 23.3 MW | (430 Amp) 23.9 MW
|  | 10) 33/11KV, 6.3 MVA | (90 Amp) 5 MW | (95 Amp) 5.3 MW
*Due to insulation problem, 110/33KV, 30MVA -II is being used for 33/11KV tranformation for local 11KV feed.
Division-XI, Tivim | [5 empty] | 2019-05-01
| 220/33/11 KV , 50MVAX2 , 1x6.3 MVA Amona Sub-station in Bicholim taluka | 1) 50 MVA- ICT-I | 34.37 | 22.74
|  | 2) 50 MVA- ICT- II | 26.49 | 19.34
|  | 3) 6.3 MVA | 2.3 | 1.3
| 220/110/33/11 KV , (3 x 100 MVA 220/110 KV, 2 x 50 MVA and 2 x 40 MVA, 110/33 KV, 2 x 10 MVA, 33/11 KV) | 3 x 100 MVA, 220/110 KV (Connected in parallel) | 216 | 165
|  | 40 MVA, 110/33 KV Tr - 1 | 27 | 22
|  | 50 MVA, 110/33 KV Tr - 2 | 27 | 22
|  | 40 MVA, 110/33 KV Tr - 3 | 36 | 29
|  | 50 MVA, 110/33 KV Tr - 4 | 46 | 35
|  | 10 MVA, 33/11 KV Tr - 1 | 5.5 | 3.5
|  | 10 MVA, 33/11 KV Tr - 2 | 6.5 | 3
Division-XVI, Margao | [5 empty] | 2019-05-01
Sub Div.-I, Benaulim
| 33/11KV Benaulim S/S | 6.3MVA PTR-I | 85 Amps | 60 Amps
|  | 6.3MVA PTR-II | 103 Amps | 75 Amps
|  | 6.3MVA PTR-III | 106 Amps | 80 Amps
| 33/11KV Carmona | i) 6.3MVA | 85 Amps | 35 Amps
Sub Div. II, Chinchinim
| 33/11KV Velim S/S | i) 6.3MVA | 66Amps | 18Amps
|  | ii) 6.3MVA | 130Amps | 73Amps
Sub Div.-III, Canacona
| 33/11KV Canacona S/S | i) 6.3MVA | 79 Amps | 44Amps
|  | ii) 6.3MVA | 58Amps | 42Amps
| 33/11KV Muthal/Paiguinim | i) 6.3MVA | 48Amps | 32Amps
Sub Div.-IV, Cuncolim
| 33/11KV Cuncolim S/S | i) 6.3MVA | 90Amps | 78Amps
|  | ii)6.3MVA | 89Amps | 79Amps
|  | iii)10MVA | 107Amps | 97Amps
Division-XII, Xeldem | [5 empty] | 2019-05-01
1 | 33/11 KV 6.3 MVA Xeldem Substation | 6.3 MVA – 1 No. | 5.25 (11 KV Peak hour loading -276 A) | 2.85 (11 KV Off peak hour loading – 150a) |  |  | 0.0047325
2 | 220/110/33/11 KV Xeldem Substation | 100 MVA –I | 65.72 (110 KV Peak hour loading -345 A) | 40.00 (110 KV Off peak hour loading – 210 A)
3 | 220/110/33/11 KV Xeldem Substation | 100 MVA –II | 72.39 (110 KV Peak hour loading -380 A) | 45.72 (110 KV Off peak hour loading – 240 A)
4 | 220/110/33/11 KV Xeldem Substation | 50 MVA | 31.43 (33 KV Peak hour loading -530 A) | 16.00 (33 KV Off peak hour loading – 280 A)
5 | 220/110/33/11 KV Xeldem Substation | 40 MVA – I | 32.23 (33 KV Peak hour loading -564 A) | 18.28 (33 KV Off peak hour loading – 320 A)
6 | 220/110/33/11 KV Xeldem Substation | 40 MVA – II | 32.23 (33 KV Peak hour loading -564 A) | 18.28 (33 KV Off peak hour loading – 320 A)
7 | 220/33KV Cuncolim Substation | 50 MVA - I | 0 MVA | 0 MVA
8 | 220/33KV Cuncolim Substation | 50 MVA- II | 36.84 MVA | 21.00 MVA
9 | 220/33KV Cuncolim Substation | 50 MVA - III | 21.00 MVA | 15.79 MVA
Division-X, Ponda | [5 empty] | 2019-05-01
1 | 33/11KV Colony S/S Sub div - I Div-X Ponda | Sl No 8973-1 Capacity:-6.3 MVA Make:- Voltamp Transformer ltd Baroda Year of Mfg:- 2007 | 6.2 (20.00 Hrs) | 5.4 (07.00 Hrs)
2 |  | Sl No. 21264/2 Capacity:-6.3 MVA Make:- Voltamp Transformer ltd Baroda Year of Mfg:- 2009 | Out of service from 16.10.2018 | Out of service from 16.10.2018
3 | 33/11KV Dharbandora S/S Sub div - II Div-X Ponda | Sl No. MT 4556 Capacity:-6.3 MVA Make:- CGL ltd Year of Mfg:- 2002 | 3.4(19.30 Hrs) | 2.8(10.00 Hrs)
4 | 33/11KV Bethora S/S Sub div - II Div-X Ponda | Sl No. B-2831 Capacity:-6.3 MVA Make:- Alstom Year of Mfg:- 2000 | 3.23 (19.30 Hrs) | 2.97 (10.00 Hrs)
5 | 33/11KV Shiroda S/S Sub div - II Div-X Ponda | Sl No. KT-6300/23 Capacity:-6.3 MVA Make:- Kanohar Year of Mfg:- 2007 | 2.25 (19.30 Hrs) | 1.88 (10.00 Hrs)
6 | 33/11KV Kundai S/S Sub div - III Div-X Ponda | Sl No 600005720 Capacity :-10MVA (I) Make:- Viajay Electricals Year of Mfg;- 2011 | 7.1 (12.00Hr) | 6.2(20.00Hrs)
7 |  | Sl No 600005721 Capacity :-10MVA (2) Make:- Viajay Electricals Year of Mfg:- 2011 | 8.65(12.00Hr) | 7.9(19.00Hrs)
8 | 33/11KV Madkai S/S Sub div - III Div-X Ponda | Sl No:-1796 Capacity :-6.3MVA Make:- Emco Ltd Year of Mfg:- 2006 | 3.29 (11.00Hrs) | 2.47(20.00Hrs)
Division-V, Bicholim | [5 empty] | 2019-05-01
| 33/11 KV , 3x6.3 MVA Bicholim Sub-station | 6.3 MVA(I) - 1 No | 5.28 (Peak hour loading - 277 A) | 2.10 (Off Peak hour loading - 110 A) |  |  | 0.277 | 1.7321 | 11 | 0.9 | 4.7498
|  | 6.3 MVA(II) - 1 No | 5.01 (Peak hour loading - 263 A) | 2.00 (Off Peak hour loading - 105)
|  | 6.3 MVA(III) - 1 No | 4.42 (Peak hour loading - 232 A) | 2.04 (Off Peak hour loading - 107)
| 33/11 KV , 1x10 MVA, Sankhali Sub-station | 10 MVA - 1 No. | 7.14 (Peak hour loading - 375 A) | 3.52 (Off Peak hour loading - 185A)
| 33/11 KV , 1x6.3 MVA Pale Sub-station | 6.3 MVA - 1 No | 1.56 (Peak hour loading - 82 A) | 0.86 (Off Peak hour loading - 45 A)
| 33/11 KV , 2x6.3 MVA Valpoi Sub-station | 6.3 MVA (I) - 1 No | 4.46 ( Peak hour loading - 234 A) | 3.45 ( Off Peak hour loading-181A)
|  | 6.3 MVA (II) - 1 No | 3.03 ( Peak hour loading- 159 A) | 2.61 (Off Peak hour loading-137A)
Division-I, Panaji
| Corlim Substation | 6.3 MVA-I | 45 | 30
|  | 6.3 MVA-I | 65 | 50
|  | 10 MVA | 146 | 120
| Altinho Substation | 6.3 MVA-I | 80 | 30
|  | 6.3 MVA-II | 80 | 38
|  | 8 MVA -III | 107 | 39
| EDC | 10 MVA -I | 91 | 35
|  | 8 MVA -II | 92 | 48
| Campal | 10 MVA - I | 143 | 73
|  | 6.3 MVA - II | 40 | 19
| Bambolim | 6.3 MVA-I | 95 | 60
|  | 6.3 MVA-II | 96 | 65
| Pilar | 6.3 MVA-I | 90 | 50
|  | 3.15 MVA-II | NOT CHARGED QUOTATION INVITED FOR REPAIR
| Nagali Hill | 10 MVA -I | 121 | 105
| NIO Substation | 6.3 MVA -I | 90 | 70
Division-XVII, Mapusa | [5 empty] | 2019-05-01
1 | Pernem-Sub station | Incomer - I 6.3 MVA Transformer - I | 3.95 MVA (Peak hour loading - 69 A 33 KV side) | 3.44 MVA (Off Peak hour loading - 60 A 33 KV side)
|  |  | 3.82 MVA (peak hour loading - 200 A 11 KV side) | 3.21 MVA (off peak hour loading - 168 A 11 KV side)
2 | Pernem-Sub station | Incomer - II 6.3 MVA Transformer - II | 4.58 MVA (Peak hour loading - 80 A 33 KV side) | 4.12 KVA (Off peak hour loading - 72 A 33 KV side ) |  | 252 | 0.252 | 1.7321 | 11 | 0.97 | 4.6572
|  |  | 4.74 MVA ( Peak hour loading - 248 A 11 KV side ) | 4.12 MVA (off peak hour loading - 216 A 11 KV side)
Sub Div.- II, Mapusa
3 | 6.3MVA 33/11KV Nachinola S/S | 6.3/8 MVA-1 No | 6.4MVA (Peak hour loading - 327 A 11KV Side) | 4 MVA (Off Peak hour loading - 205 A 11KV side)
|  |  | 111 A - 33KV Side | 67 A - 33KV side
Sub Div.- III, Agarwada
4 | Power Transformer I ( 6.3/ 8MVA) | 6.3/8 MVA-1 No | 33 kv side 70 amps max | 33 kv Side 42.6 amps min
|  |  | 11 kv Side 214 amps max | 11 kv side 126 amps min
5 | Power Transformer II (6.3 MVA) | 6.3 MVA-1 No | 33 kv side 77.4 amps max | 33 kv Side 40.8 amps min
|  |  | 11 kv Side 246 amps max | 11 kv side 130 amps min
Division-IV, Margao | [5 empty] | 2019-05-01
| 33/11KV Aquem Sub-station | TR-1, 10MVA (new) | 120 A | 56 A | 33KV Side
|  | TR-II, 10MVA | 143 A | 63 A
|  | TR-III, 6.3MVA | 36 A | 12 A | 33KV Side
| 33/11KV Monte Sub-station | TR-I 6.3MVA | 44 A | 11 A
|  | TR-II 6.3MVA | 105 A | 39 A | 33KV Side
|  | TR-III, 6.3MVA | 57 A | 16 A
| 33/11KV Fatorda Sub-station | TR-I, 10MVA | 106 Amps | 44 A | 33KV Side
|  | TR-II, 6.3MVA | 93 A | 40 A
|  | TR-III, 6.3MVA | 75 A | 37 A | 33KV Side
| 33/11KV KRC Sub-station | TR1, 10MVA (new) | 126 A | 42 A
|  | TR-II, 6.3MVA | No Load | No Load | 33KV Side
| 33/11KV Nessai Sub-station | TR-I, 6.3MVA | 76 A | 39 A
|  | TR-II, 6.3MVA | 74 A | 29 A
| 33/11KV Raia Sub-station | TR-I, 6.3MVA | 54 A | 27 A | 33KV Side
|  | TR-II, 6.3MVA | 84 A | 43 A
Division-VI, Mapusa | [5 empty] | 2019-05-01
S/D-I(U) Mapusa
1 | Mapusa Sub-Station | 10MVA -I | 9.2 | 8.7
2 |  | 10MVA -II | 8.9 | 8.5
3 |  | 10MVA- III | 9.9 | 9.5
4 |  | 8MVA | 6.6 | 6.4
S/D-II Porvorim
1 | Porvorim Sub-Station | 6.3MVA | 4.977 | 5.481
2 |  | 8 MVA | 6.16 | 5.2
3 |  | 10 MVA | 8.7 | 7.5
S/D-III Mapusa
1 | Nagoa Sub-Station | 8 MVA | 7.03 | 6.344
2 |  | 6.3 MVA | 5.48 | 4.8
3 |  | 10 MVA | 9.6 | 7.77
S/D-IV Calangute
1 | Saligao Substation | 6.3MVA | 3.52 | 3.2
2 |  | 6.3/8MVA | 4.56 | 4.22
3 |  | 10MVA | 6.42 | 6.12
4 | Candolim substation | 6.3MVA | 2.145 | 2.1
|  | 6.3/8MVA | 6.31 | 6.23
5 |  | 10MVA | 2.2 | 2.02
Division-XIV, SUB-DIV-II, VERNA | [5 empty] | 2019-05-01
1 | 110/33 KV sub-station, Verna | 40MVA -I | 29.7 | 25.7
2 | 110/33 KV sub-station, Verna | 40MVA -II | 29.1 | 24.6
3 | 110/33 KV sub-station, Verna | 50MVA TR | 37.1 | 31.4
4 | 33/11KV sub-station, Verna | 6.3 MVA -I | 4.8 | 3.6
5 | 33/11KV sub-station, Verna | 10MVA -I | 7.6 | 5.9
6 | 33/11KV sub-station, Verna | 10MVA -II | 7.3 | 6.4
SUB-DIV-III, VERNA
7 | 33/11KV Majorda Sub-Station | 10 MVA | 6.17 | 3.14
8 | 33/11KV Majorda Sub-Station | 6.3MVA | 3.65 | 2.1